## Products
PRODUCT NAME | ALB-RB
|  |  |  | ALB02RBMNADBT00 | ALB03RBMNADBT00 | ALB04RBMNADBT00 | ALB05RBMNADBT00 | ALB06RBMNADBT00 | ALB07RBMNADBT00
Air flow | Nom. |  | m³/h | 300 | 600 | 1,200 | 1,500 | 2,500 | 3,000
Power input | Nom. |  | kW | 0.12 | 0.27 | 0.44 | 0.57 | 1.01 | 1.24
Specific fan power (SFPv) | kW/(m³/s) |  |  | 1.24 | 1.49 | 1.25 | 1.31 | 1.42 | 1.46
Dimensions | Supply | Net overall height | mm | 150 | 200 | 300 | 300 | 400 | 400
|  | Overall width | mm | 250 | 400 | 500 | 500 | 700 | 700
| Unit | Height overall | mm | 280 | 350 | 415 | 415 | 500 | 500
|  | Width | mm | 920 | 1,100 | 1,600 | 1,600 | 2,000 | 2,000
|  | Length | mm | 1,660 | 1,800 | 2,000 | 2,000 | 2,000 | 2,000
Weight | Unit |  | kg | 125 | 180 | 270 | 280 | 355 | 360
External static pressure | Nom. |  | Pa | 100 | 100 | 100 | 100 | 100 | 100
Sound pressure level | Nom. |  | dBA | 33 | 39 | 39 | 35 | 43 | 40
General | Supplier/Manufacturer details | Name or trademark |  | Daikin Applied Europe | Daikin Applied Europe | Daikin Applied Europe | Daikin Applied Europe | Daikin Applied Europe | Daikin Applied Europe
Type of product |  |  |  | Bidirectional NRVU | Bidirectional NRVU | Bidirectional NRVU | Bidirectional NRVU | Bidirectional NRVU | Bidirectional NRVU
Type of drive |  |  |  | variable speed drive | variable speed drive | variable speed drive | variable speed drive | variable speed drive | variable speed drive
Heat recovery system |  |  |  | other | other | other | other | other | other
Thermal efficiency | % |  |  | 77.8 (0.000) | 79.6 (0.000) | 81.9 (0.000) | 80.4 (0.000) | 82.1 (0.000) | 80.7 (0.000)
Nominal flow rate | m³/s |  |  | 0.15 | 0.32 | 0.40 | 0.54 | 0.76 | 1.01
Effective electric power input | kW |  |  | 0.31 | 0.69 | 0.67 | 0.92 | 1.26 | 1.72
Internal specific fan power | W/(m³/s) |  |  | 842 (0.000) | 1,181 (0.000) | 631 (0.000) | 787 (0.000) | 810 (0.000) | 1,010 (0.000)
Face velocity | m/s |  |  | 1.5 | 2.0 | 1.4 | 1.9 | 1.7 | 2.3
External pressure | Pa |  |  | 30 | 30 | 30 | 30 | 30 | 30
Internal pressure drop | Pa |  |  | 227 (0.000) | 351 (0.000) | 169 (0.000) | 244 (0.000) | 221 (0.000) | 315 (0.000)
Fan efficiency | % |  |  | 53 (0.000) | 59 (0.000) | 53 (0.000) | 61 (0.000) | 53 (0.000) | 61 (0.000)
Maximum external leakage | % |  |  | <4 | <3 | <4 | <3 | <3 | <2
Maximum internal leakage | % |  |  | <3 | <2 | <3 | <2 | <2 | <2
Filter service warning |  |  |  | Displayed on controller | Displayed on controller | Displayed on controller | Displayed on controller | Displayed on controller | Displayed on controller
Sound power level (Lwa) | dB |  |  | 53 | 61 | 62 | 58 | 63 | 60
Instructions for pre-/disassembly |  |  |  | http://www.daikinapplied.eu/en/index/page/download/1350 | http://www.daikinapplied.eu/en/index/page/download/1350 | http://www.daikinapplied.eu/en/index/page/download/1350 | http://www.daikinapplied.eu/en/index/page/download/1350 | http://www.daikinapplied.eu/en/index/page/download/1350 | http://www.daikinapplied.eu/en/index/page/download/1350
Current | Nom. |  | A | 0.52 | 1.17 | 1.91 | 2.48 | 4.39 | 5.39
Power supply | Phase |  |  | 1~ | 1~ | 1~ | 1~ | 1~ | 1~
| Frequency |  | Hz | 50/60 | 50/60 | 50/60 | 50/60 | 50/60 | 50/60
| Voltage |  | V | 220-240 | 220-240 | 220-240 | 220-240 | 220-240 | 220-240
Notes_Description |  |  |  | Clean/replace Filter(s) when maximum pressure drop is reached or when warning is displayed on HMI controller | Clean/replace Filter(s) when maximum pressure drop is reached or when warning is displayed on HMI controller | Clean/replace Filter(s) when maximum pressure drop is reached or when warning is displayed on HMI controller | Clean/replace Filter(s) when maximum pressure drop is reached or when warning is displayed on HMI controller | Clean/replace Filter(s) when maximum pressure drop is reached or when warning is displayed on HMI controller | Clean/replace Filter(s) when maximum pressure drop is reached or when warning is displayed on HMI controller