## Products
PRODUCT NAME | EWAD-CZXL
[5 empty] | EWAD670CZXL | EWAD740CZXL | EWAD830CZXL | EWAD900CZXL | EWADC10CZXL | EWADC11CZXL | EWADC12CZXL | EWADC13CZXL | EWADC14CZXL | EWADC15CZXL | EWADC16CZXL | EWADC17CZXL | EWADC18CZXL
Sound pressure level | Cooling |  | Nom. | dBA | 77.5 (2) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 80 | 80 | 80
Operation range | Air side | Cooling | Min. | °CDB | -18 | -18 | -18 | -18 | -18 | -18 | -18 | -18 | -18 | -18 | -18 | -18 | -18
|  |  | Max. | °CDB | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
| Water side | Cooling | Max. | °CDB | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
|  |  | Min. | °CDB | -8 | -8 | -8 | -8 | -8 | -8 | -8 | -8 | -8 | -8 | -8 | -8 | -8
Refrigerant circuit | Charge |  |  | kg | 141
Compressor | Oil |  | Charged volume | l | 32 | 32 | 35 | 38 | 38 | 38 | 44 | 50 | 50 | 50 | 57 | 63 | 69
| Quantity |  |  |  | Semi-hermetic single screw compressor
Weight | Operation weight |  |  | kg | 6,430 | 6,530 | 7,140 | 7,390 | 8,160 | 8,160 | 9,240 | 9,640 | 10,260 | 10,600 | 12,640 | 13,460 | 14,210
| Unit |  |  | kg | 6,170 | 6,280 | 6,900 | 7,150 | 7,720 | 7,720 | 8,850 | 9,250 | 9,880 | 10,220 | 11,790 | 12,610 | 13,340
Air heat exchanger | Type |  |  |  | High efficiency fin and tube type with integral subcooler
Refrigerant | Circuits |  |  | Quantity | 2
| Type |  |  |  | R-134a
Fan motor | Input |  | Cooling | W | 1.75
| Speed | Cooling | Nom. | rpm | 900
| Drive |  |  |  | DOL
Cooling capacity | Nom. |  |  | kW | 672 (1)
Piping connections | Piping connections-=-Evaporator water inlet outlet od |  |  |  | 168.3mm
Water heat exchanger | Water volume |  |  | l | 263 | 248 | 241 | 241 | 441 | 441 | 383 | 383 | 374 | 374 | 850 | 850 | 871
| Water pressure drop | Cooling | Nom. | kPa | 80 | 82.7 | 58.2 | 64.6 | 63.2 | 70.3 | 47 | 52.1 | 61.9 | 71.9 | 62.8 | 69.1 | 65.1
| Water flow rate | Cooling | Nom. | l/s | 32.00
| Insulation material |  |  |  | Single pass shell & tube
Power input | Cooling |  | Nom. | kW | 245 (1) | 238 | 269.5 | 309.2 | 343.3 | 379.9 | 404.3 | 446.6 | 493.7 | 538.4 | 564.3 | 595.9 | 618.7
Sound power level | Cooling |  | Nom. | dBA | 98.6 | 99 | 100 | 100 | 100 | 100 | 101 | 101 | 101 | 101 | 103 | 103 | 103
Safety devices | Item |  |  | 01 | Water freeze protection controller
Dimensions | Unit |  | Width | mm | 2,285 | 2,285 | 2,285 | 2,285 | 2,285 | 2,285 | 2,285 | 2,285 | 2,285 | 2,285 | 2,285 | 2,285 | 2,285
|  |  | Depth | mm | 6,725 | 6,725 | 7,625 | 7,625 | 8,525 | 8,525 | 10,325 | 10,325 | 11,625 | 12,525 | 12,525 | 13,425 | 14,325
|  |  | Height | mm | 2,540 | 2,540 | 2,540 | 2,540 | 2,540 | 2,540 | 2,540 | 2,540 | 2,540 | 2,540 | 2,540 | 2,540 | 2,540
Capacity control | Minimum capacity |  |  | % | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 13 | 13 | 13
| Method |  |  |  | Stepless
Casing | Colour |  |  |  | Galvanized and painted steel sheet
Fan | Diameter |  |  | mm | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800
| Air flow rate |  | Nom. | l/s | 54,188 | 65,026 | 75,863 | 75,863 | 86,701 | 86,701 | 108,376 | 108,376 | 119,214 | 130,051 | 129,455 | 140,143 | 151,130
| Speed |  |  | rpm |  | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900
| Quantity |  |  |  | Direct propeller
Eer |  |  |  |  | 5.07
Fans | Nominal running current (RLA) |  |  | A | 40 | 48 | 56 | 56 | 64 | 64 | 80 | 80 | 88 | 96 | 96 | 104 | 112
Compressor 3 | Maximum running current |  |  | A | [10 empty] | 345 | 399 | 345
Compressor | Maximum running current |  |  | A | 205 | 240 | 240 | 288 | 288 | 345 | 345 | 399 | 399 | 493 | 345 | 345 | 399
| Voltage range |  | Min. | % | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10
|  |  | Max. | % | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
| Voltage |  |  | V | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
| Starting method |  |  |  | 3~
Compressor 2 | Maximum running current |  |  | A | 205 | 240 | 288 | 288 | 345 | 345 | 399 | 399 | 493 | 493 | 345 | 345 | 399
Power supply | Voltage range |  | Max. | % | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  |  | Min. | % | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10
| Frequency |  |  | Hz | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
| Voltage |  |  | V | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
| Phase |  |  |  | 3~
Unit | Max unit current for wires sizing |  |  | A | 494 | 535 | 588 | 633 | 728 | 816 | 825 | 877 | 1,000 | 1,125 | 1,224 | 1,253 | 1,283
| Maximum running current |  |  | A | 451
| Maximum starting current |  |  | A | 322
| Nominal running current (RLA) |  | Cooling | A | 362
Notes |  |  |  |  | Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1
Cooling capacity | Nom. |  |  | kW |  | 734.1 | 828.5 | 898.2 | 1,033 | 1,090 | 1,232 | 1,303 | 1,444 | 1,538 | 1,616 | 1,701 | 1,795
| Rated |  |  | kW |  | 734.12 | 828.54 | 898.15 | 1,033 | 1,090.04 | 1,232 | 1,303.04 | 1,444.04 | 1,538 | 1,616.03 | 1,701 | 1,795
Capacity control | Method |  |  |  |  | Variable | Variable | Variable | Variable | Variable | Variable | Variable | Variable | Variable | Variable | Variable | Variable
EER | [5 empty] | 3.072 | 3.075 | 2.904 | 3.008 | 2.869 | 3.047 | 2.919 | 2.926 | 2.856 | 2.863 | 2.855 | 2.9
ESEER | [5 empty] | 4.72 | 4.89 | 4.88 | 4.91 | 4.7 | 4.7 | 4.51 | 4.73 | 4.83 | 4.59 | 4.62 | 4.61
IPLV | [5 empty] | 5.68 | 5.72 | 5.79 | 5.73 | 5.56 | 5.58 | 5.45 | 5.61 | 5.75 | 5.65 | 5.46 | 5.29
SEER | [5 empty] | 4.85 | 4.98 | 5 | 5.13 | 5.02 | 5.22 | 5.19 | 5.23 | 5.11 | 5.07 | 5.15 | 5.26
Casing | Colour |  |  |  |  | Ivory white | Ivory white | Ivory white | Ivory white | Ivory white | Ivory white | Ivory white | Ivory white | Ivory white | Ivory white | Ivory white | Ivory white
| Material |  |  |  |  | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet
Water heat exchanger | Type |  |  |  |  | Shell and tube | Shell and tube | Shell and tube | Shell and tube | Shell and tube | Shell and tube | Shell and tube | Shell and tube | Shell and tube | Shell and tube | Shell and tube | Shell and tube
| Water flow rate | Cooling | Nom. | l/s |  | 35.2 | 39.7 | 43 | 49.5 | 52.3 | 59 | 62.4 | 69.2 | 73.7 | 77.4 | 81.5 | 86
| Insulation material |  |  |  |  | Closed cell | Closed cell | Closed cell | Closed cell | Closed cell | Closed cell | Closed cell | Closed cell | Closed cell | Closed cell | Closed cell | Closed cell
Air heat exchanger | Type |  |  |  |  | High efficiency fin and tube type | High efficiency fin and tube type | High efficiency fin and tube type | High efficiency fin and tube type | High efficiency fin and tube type | High efficiency fin and tube type | High efficiency fin and tube type | High efficiency fin and tube type | High efficiency fin and tube type | High efficiency fin and tube type | High efficiency fin and tube type | High efficiency fin and tube type
Heat exchanger | Indoor side |  |  |  |  | water | water | water | water | water | water | water | water | water | water | water | water
| Outdoor side |  |  |  |  | Air | Air | Air | Air | Air | Air | Air | Air | Air | Air | Air | Air
Fan | Quantity |  |  |  |  | 12 | 14 | 14 | 16 | 16 | 20 | 20 | 22 | 24 | 24 | 26 | 28
| Type |  |  |  |  | Direct propeller | Direct propeller | Direct propeller | Direct propeller | Direct propeller | Direct propeller | Direct propeller | Direct propeller | Direct propeller | Direct propeller | Direct propeller | Direct propeller
| Air flow rate | Cooling | Rated | m³/h |  | 234,093.6 | 273,106.8 | 273,106.8 | 312,123.6 | 312,123.6 | 390,153.6 | 390,153.6 | 429,170.4 | 468,183.6 | 466,038 | 504,514.8 | 544,068
Fan motor | Drive |  |  |  |  | DOL | DOL | DOL | DOL | DOL | DOL | DOL | DOL | DOL | DOL | DOL | DOL
| Input |  | Cooling | W |  | 21,000 | 24,500 | 24,500 | 28,000 | 28,000 | 35,000 | 35,000 | 38,500 | 42,000 | 42,000 | 45,500 | 49,000
Compressor | Quantity |  |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3
| Type |  |  |  |  | Driven vapour compression | Driven vapour compression | Driven vapour compression | Driven vapour compression | Driven vapour compression | Driven vapour compression | Driven vapour compression | Driven vapour compression | Driven vapour compression | Driven vapour compression | Driven vapour compression | Driven vapour compression
| Driver |  |  |  |  | Electric motor | Electric motor | Electric motor | Electric motor | Electric motor | Electric motor | Electric motor | Electric motor | Electric motor | Electric motor | Electric motor | Electric motor
Refrigerant | Type |  |  |  |  | R-134a | R-134a | R-134a | R-134a | R-134a | R-134a | R-134a | R-134a | R-134a | R-134a | R-134a | R-134a
| GWP |  |  |  |  | 1,430 | 1,430 | 1,430 | 1,430 | 1,430 | 1,430 | 1,430 | 1,430 | 1,430 | 1,430 | 1,430 | 1,430
| Circuits |  | Quantity |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3
| Charge |  |  | kg |  | 146 | 162 | 162 | 200 | 200 | 250 | 250 | 250 | 280 | 320.1 | 339.9 | 350.1
Charge | Per circuit |  |  | TCO2Eq |  | 104.4 | 115.8 | 115.8 | 143.0 | 143.0 | 178.8 | 178.8 | 178.8 | 200.2 | 152.5 | 162.1 | 166.8
Piping connections | Evaporator water inlet/outlet (OD) |  |  |  |  | 168.3mm | 168.3mm | 168.3mm | 219.1mm | 219.1mm | 219.1mm | 219.1mm | 219.1mm | 219.1mm | 273mm | 273mm | 273mm
Space cooling | A Condition 35°C |  | Pdc | kW |  | 734.12 | 828.54 | 898.15 | 1,033 | 1,090.04 | 1,232 | 1,303.04 | 1,444.04 | 1,538 | 1,616.03 | 1,701 | 1,795
|  |  | EERd |  |  | 3.07 | 3.08 | 2.9 | 3.01 | 2.87 | 3.05 | 2.92 | 2.93 | 2.86 | 2.86 | 2.86 | 2.9
| B Condition 30°C |  | Pdc | kW |  | 544.32 | 613.99 | 665.66 | 767.84 | 807.98 | 916.02 | 965.44 | 1,070.12 | 1,140.36 | 1,197.57 | 1,267.27 | 1,330.55
|  |  | EERd |  |  | 4.43 | 4.55 | 4.61 | 4.68 | 4.59 | 4.73 | 4.68 | 4.73 | 4.67 | 4.62 | 4.65 | 4.76
| C Condition 25°C |  | Pdc | kW |  | 346.27 | 390.39 | 423.29 | 488.27 | 513.87 | 582.31 | 613.79 | 680.51 | 725.3 | 761.56 | 805.97 | 846.14
|  |  | EERd |  |  | 5.46 | 5.56 | 5.63 | 5.72 | 5.63 | 5.82 | 5.81 | 5.8 | 5.67 | 5.67 | 5.75 | 5.88
| D Condition 20°C |  | Pdc | kW |  | 154.89 | 174.58 | 189.3 | 218.35 | 229.81 | 260.35 | 274.43 | 304.28 | 324.34 | 340.36 | 360.28 | 378.26
|  |  | EERd |  |  | 6.21 | 6.45 | 6.39 | 6.6 | 6.43 | 6.64 | 6.7 | 6.76 | 6.45 | 6.61 | 6.81 | 6.93
| ηs,c |  |  | % |  | 191 | 196.2 | 197 | 202.2 | 197.8 | 205.8 | 204.6 | 206.2 | 201.4 | 199.8 | 203 | 207.4
General | Supplier/Manufacturer details |  | Name and address |  |  | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy
LW(A) Sound power level (according to EN14825) | dB(A) |  |  |  |  | 99 | 100 | 100 | 100 | 100 | 101 | 101 | 101 | 101 | 103 | 103 | 103
Cooling | Cdc (Degradation cooling) |  |  |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Standard rating conditions used | [5 empty] | Low temperature application | Low temperature application | Low temperature application | Low temperature application | Low temperature application | Low temperature application | Low temperature application | Low temperature application | Low temperature application | Low temperature application | Low temperature application | Low temperature application
Power consumption in other than active mode | Crankcase heater mode |  | PCK | W |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.38 | 0.38 | 0.38
| Off mode |  | POFF | W |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Standby mode | Cooling | PSB | W |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15
| Thermostat-off mode | PTO | Cooling | W |  | 0.41 | 0.39 | 0.41 | 0.42 | 0.44 | 0.41 | 0.43 | 0.46 | 0.5 | 0.76 | 0.76 | 0.72
Power supply | Phase |  |  |  |  | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~
Unit | Starting current |  | Max | A |  | 377 | 420 | 451 | 501 | 540 | 590 | 626 | 709 | 772 | 848 | 899 | 949
| Running current | Cooling | Nom. | A |  | 406 | 442 | 485 | 537 | 591 | 636 | 698 | 769 | 837 | 848 | 931 | 970
|  |  | Max | A |  | 529 | 584 | 632 | 697 | 755 | 824 | 877 | 979 | 1,081 | 1,132 | 1,193 | 1,255
Compressor | Phase |  |  |  |  | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~
| Starting method |  |  |  |  | Inverter driven | Inverter driven | Inverter driven | Inverter driven | Inverter driven | Inverter driven | Inverter driven | Inverter driven | Inverter driven | Inverter driven | Inverter driven | Inverter driven
Notes | [5 empty] | Performance calculations according to EN 14511 | Performance calculations according to EN 14511 | Performance calculations according to EN 14511 | Performance calculations according to EN 14511 | Performance calculations according to EN 14511 | Performance calculations according to EN 14511 | Performance calculations according to EN 14511 | Performance calculations according to EN 14511 | Performance calculations according to EN 14511 | Performance calculations according to EN 14511 | Performance calculations according to EN 14511 | Performance calculations according to EN 14511
[6 empty] | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units
[6 empty] | Maximum starting current: unit is inverter driven. No inrush current at start up. Declared value refers to the stand-by current. | Maximum starting current: unit is inverter driven. No inrush current at start up. Declared value refers to the stand-by current. | Maximum starting current: unit is inverter driven. No inrush current at start up. Declared value refers to the stand-by current. | Maximum starting current: unit is inverter driven. No inrush current at start up. Declared value refers to the stand-by current. | Maximum starting current: unit is inverter driven. No inrush current at start up. Declared value refers to the stand-by current. | Maximum starting current: unit is inverter driven. No inrush current at start up. Declared value refers to the stand-by current. | Maximum starting current: unit is inverter driven. No inrush current at start up. Declared value refers to the stand-by current. | Maximum starting current: unit is inverter driven. No inrush current at start up. Declared value refers to the stand-by current. | Maximum starting current: unit is inverter driven. No inrush current at start up. Declared value refers to the stand-by current. | Maximum starting current: unit is inverter driven. No inrush current at start up. Declared value refers to the stand-by current. | Maximum starting current: unit is inverter driven. No inrush current at start up. Declared value refers to the stand-by current. | Maximum starting current: unit is inverter driven. No inrush current at start up. Declared value refers to the stand-by current.
[6 empty] | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current. | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current. | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current. | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current. | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current. | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current. | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current. | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current. | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current. | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current. | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current. | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.
[6 empty] | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current
[6 empty] | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage.
[6 empty] | Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water
[6 empty] | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.
[6 empty] | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS).
[6 empty] | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels. | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels. | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels. | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels. | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels. | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels. | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels. | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels. | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels. | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels. | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels. | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.