## Products
PRODUCT NAME | EWLQ-G-SS
[5 empty] | EWLQ090G-SS | EWLQ100G-SS | EWLQ120G-SS | EWLQ130G-SS | EWLQ150G-SS | EWLQ170G-SS | EWLQ190G-SS | EWLQ210G-SS | EWLQ240G-SS | EWLQ300G-SS | EWLQ360G-SS
Cooling capacity | Nom. |  |  | kW | 86.5 (1) | 98.4 (1) | 110 (1) | 125 (1) | 139 (1) | 160 (1) | 181 (1) | 206 (1) | 231 (1) | 290 (1) | 346 (1)
Capacity control | Method |  |  |  | Step | Step | Step | Step | Step | Step | Step | Step | Step | Step | Step
| Minimum capacity |  |  | % | 50.0 | 43.0 | 50.0 | 44.0 | 50.0 | 45.0 | 50.0 | 43.0 | 50.0 | 40.0 | 50.0
Power input | Cooling |  | Nom. | kW | 22.4 (1) | 25.8 (1) | 29.2 (1) | 33.0 (1) | 36.8 (1) | 42.0 (1) | 47.0 (1) | 54.2 (1) | 59.9 (1) | 75.6 (1) | 91.8 (1)
EER |  |  |  |  | 3.86 (1) | 3.81 (1) | 3.78 (1) | 3.79 (1) | 3.79 (1) | 3.80 (1) | 3.86 (1) | 3.80 (1) | 3.85 (1) | 3.84 (1) | 3.77 (1)
Dimensions | Unit |  | Height | mm | 1,066 | 1,066 | 1,066 | 1,066 | 1,066 | 1,066 | 1,066 | 1,066 | 1,066 | 1,186 | 1,186
|  |  | Width | mm | 928 | 928 | 928 | 928 | 928 | 928 | 928 | 928 | 928 | 928 | 928
|  |  | Depth | mm | 2,743 | 2,743 | 2,743 | 2,743 | 2,743 | 2,743 | 2,743 | 2,743 | 2,743 | 2,743 | 2,743
Weight | Unit |  |  | kg | 494 | 578 | 686 | 714 | 742 | 773 | 807 | 838 | 852 | 967 | 1,046
| Operation weight |  |  | kg | 525 | 615 | 729 | 760 | 791 | 826 | 863 | 901 | 916 | 1,044 | 1,134
Casing | Colour |  |  |  | Ivory white | Ivory white | Ivory white | Ivory white | Ivory white | Ivory white | Ivory white | Ivory white | Ivory white | Ivory white | Ivory white
| Material |  |  |  | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet
Water heat exchanger - evaporator | Type |  |  |  | Plate heat exchanger | Plate heat exchanger | Plate heat exchanger | Plate heat exchanger | Plate heat exchanger | Plate heat exchanger | Plate heat exchanger | Plate heat exchanger | Plate heat exchanger | Plate heat exchanger | Plate heat exchanger
| Water volume |  |  | l | 6 | 8 | 8 | 10 | 12 | 13 | 15 | 17 | 17 | 27 | 34
| Water flow rate |  | Nom. | l/s | 4.2 | 4.7 | 5.3 | 6.0 | 6.7 | 7.7 | 8.7 | 9.8 | 11.1 | 13.9 | 16.6
| Water pressure drop | Cooling | Nom. | kPa | 44 | 44 | 35 | 29 | 29 | 31 | 33 | 30 | 38 | 41 | 41
| Insulation material |  |  |  | Closed cell | Closed cell | Closed cell | Closed cell | Closed cell | Closed cell | Closed cell | Closed cell | Closed cell | Closed cell | Closed cell
Compressor | Type |  |  |  | Scroll compressor | Scroll compressor | Scroll compressor | Scroll compressor | Scroll compressor | Scroll compressor | Scroll compressor | Scroll compressor | Scroll compressor | Scroll compressor | Scroll compressor
| Quantity |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Oil |  | Charged volume | l | 7 | 8 | 9 | 11 | 14 | 13 | 13 | 13 | 13 | 13 | 13
Sound power level | Cooling |  | Nom. | dBA | 80 | 83 | 85 | 87 | 88 | 88 | 88 | 90 | 92 | 93 | 93
Sound pressure level | Cooling |  | Nom. | dBA | 64 | 67 | 69 | 70 | 72 | 72 | 72 | 74 | 76 | 76 | 77
Operation range | Evaporator | Cooling | Min. | °CDB | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10
|  |  | Max. | °CDB | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
| Condenser | Cooling | Min. | °CDB | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  |  | Max. | °CDB | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Refrigerant | Type |  |  |  | R-410A | R-410A | R-410A | R-410A | R-410A | R-410A | R-410A | R-410A | R-410A | R-410A | R-410A
| GWP |  |  |  | 2,087.5 | 2,087.5 | 2,087.5 | 2,087.5 | 2,087.5 | 2,087.5 | 2,087.5 | 2,087.5 | 2,087.5 | 2,087.5 | 2,087.5
| Circuits |  | Quantity |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Piping connections | Discharge line connection |  |  | inch | 1" 5/8 | 1" 5/8 | 1" 5/8 | 1" 5/8 | 1" 5/8 | 1" 5/8 | 1" 5/8 | 1" 5/8 | 1" 5/8 | 2"1/8 | 2"1/8
| Evaporator water inlet/outlet (OD) |  |  |  | 1" 1/2 | 1" 1/2 | 2" 1/2 | 2" 1/2 | 2" 1/2 | 2" 1/2 | 2" 1/2 | 2" 1/2 | 2" 1/2 | 3" | 3"
Power supply | Phase |  |  |  | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~
| Frequency |  |  | Hz | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
| Voltage |  |  | V | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
| Voltage range |  | Min. | % | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10
|  |  | Max. | % | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Unit | Starting current |  | Max | A | 204 | 255 | 261 | 308 | 316 | 354 | 368 | 466 | 481.0 | 640 | 677
| Running current | Cooling | Nom. | A | 39 | 42 | 45 | 51 | 57 | 64 | 70 | 81 | 88 | 111 | 135
|  |  | Max | A | 59 | 66 | 72 | 80 | 88 | 102 | 116 | 131 | 145 | 183 | 221
| Max unit current for wires sizing |  |  | A | 65 | 72 | 79 | 88 | 96 | 112 | 128 | 144 | 160 | 201 | 243
Compressor | Phase |  |  |  | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~
| Voltage |  |  | V | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
| Voltage range |  | Min. | % | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10
|  |  | Max. | % | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
| Maximum running current |  |  | A | 59 | 66 | 72 | 80 | 88 | 102 | 116 | 131 | 145 | 183 | 221
| Starting method |  |  |  | Direct on line | Direct on line | Direct on line | Direct on line | Direct on line | Direct on line | Direct on line | Direct on line | Direct on line | Direct on line + part winding | Part winding
Notes |  |  |  |  | Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation. | Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation. | Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation. | Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation. | Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation. | Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation. | Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation. | Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation. | Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation. | Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation. | Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.
[5 empty] | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units
[5 empty] | Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water
[5 empty] | Its functioning relies on fluorinated greenhouse gases | Its functioning relies on fluorinated greenhouse gases | Its functioning relies on fluorinated greenhouse gases | Its functioning relies on fluorinated greenhouse gases | Its functioning relies on fluorinated greenhouse gases | Its functioning relies on fluorinated greenhouse gases | Its functioning relies on fluorinated greenhouse gases | Its functioning relies on fluorinated greenhouse gases | Its functioning relies on fluorinated greenhouse gases | Its functioning relies on fluorinated greenhouse gases | Its functioning relies on fluorinated greenhouse gases
[5 empty] | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.
[5 empty] | Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load | Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load | Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load | Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load | Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load | Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load | Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load | Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load | Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load | Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load | Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load
[5 empty] | Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current | Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current | Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current | Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current | Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current | Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current | Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current | Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current | Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current | Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current | Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current
[5 empty] | Maximum running current is based on max compressor absorbed current in its envelope | Maximum running current is based on max compressor absorbed current in its envelope | Maximum running current is based on max compressor absorbed current in its envelope | Maximum running current is based on max compressor absorbed current in its envelope | Maximum running current is based on max compressor absorbed current in its envelope | Maximum running current is based on max compressor absorbed current in its envelope | Maximum running current is based on max compressor absorbed current in its envelope | Maximum running current is based on max compressor absorbed current in its envelope | Maximum running current is based on max compressor absorbed current in its envelope | Maximum running current is based on max compressor absorbed current in its envelope | Maximum running current is based on max compressor absorbed current in its envelope
[5 empty] | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage.
[5 empty] | Maximum current for wires sizing: compressor full load ampere x 1.1 | Maximum current for wires sizing: compressor full load ampere x 1.1 | Maximum current for wires sizing: compressor full load ampere x 1.1 | Maximum current for wires sizing: compressor full load ampere x 1.1 | Maximum current for wires sizing: compressor full load ampere x 1.1 | Maximum current for wires sizing: compressor full load ampere x 1.1 | Maximum current for wires sizing: compressor full load ampere x 1.1 | Maximum current for wires sizing: compressor full load ampere x 1.1 | Maximum current for wires sizing: compressor full load ampere x 1.1 | Maximum current for wires sizing: compressor full load ampere x 1.1 | Maximum current for wires sizing: compressor full load ampere x 1.1
[5 empty] | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS).