## Products
PRODUCT NAME | EWYQ-ACV3
[5 empty] | EWYQ009ACV3 | EWYQ010ACV3 | EWYQ011ACV3
Cooling capacity | Nom. |  |  | kW | 12.2 (1), 8.60 (2) | 13.6 (1), 9.60 (2) | 11.1 (2), 15.7 (1)
Heating capacity | Nom. |  |  | kW | 9.90 (2), 10.2 (1) | 11.7 (1), 11.4 (2) | 13.8 (1), 12.9 (2)
Capacity control | Method |  |  |  | Inverter controlled | Inverter controlled | Inverter controlled
Power input | Cooling |  | Nom. | kW | 2.83 (2), 2.85 (1) | 3.28 (2), 3.41 (1) | 3.90 (2), 4.13 (1)
| Heating |  | Nom. | kW | 2.43 (1), 2.99 (2) | 2.81 (1), 3.46 (2) | 3.20 (1), 3.94 (2)
EER |  |  |  |  | 3.05 (2), 4.27 (1) | 2.93 (2), 4.00 (1) | 2.85 (2), 3.79 (1)
COP |  |  |  |  | 3.30 (2), 4.19 (1) | 3.29 (2), 4.17 (1) | 3.27 (2), 4.30 (1)
ESEER |  |  |  |  | 4.31 | 4.30 | 4.33
Dimensions | Packed unit |  | Depth | mm | 430 | 430 | 430
|  |  | Height | mm | 1,574 | 1,574 | 1,574
|  |  | Width | mm | 1,500 | 1,500 | 1,500
| Unit |  | Depth | mm | 382 | 382 | 382
|  |  | Height | mm | 1,435 | 1,435 | 1,435
|  |  | Width | mm | 1,420 | 1,420 | 1,420
Weight | Packed unit |  |  | kg | 200 | 200 | 200
| Unit |  |  | kg | 180 | 180 | 180
Packing | Material |  |  |  | PP (Straps), Wood, EPS, Carton | PP (Straps), Wood, EPS, Carton | PP (Straps), Wood, EPS, Carton
| Weight |  |  | kg | 20.0 | 20.0 | 20.0
Casing | Colour |  |  |  | Ivory white | Ivory white | Ivory white
| Material |  |  |  | Painted galvanized steel plate | Painted galvanized steel plate | Painted galvanized steel plate
Water heat exchanger | Quantity |  |  |  | 1 | 1 | 1
| Type |  |  |  | Brazed plate | Brazed plate | Brazed plate
| Water flow rate |  | Min. | l/min | 16 | 16 | 16
|  |  | Max. | l/min | 58 | 58 | 58
|  | Heating | Nom. | l/min | 28.3 (4) | 32.6 (4) | 36.9 (4)
| Water volume |  |  | l | 1.01 | 1.01 | 1.01
| Insulation material |  |  |  | Foamed synthetic elastomer | Foamed synthetic elastomer | Foamed synthetic elastomer
Air heat exchanger | Type |  |  |  | Hi-XSS (8) | Hi-XSS (8) | Hi-XSS (8)
| Empty tubeplate hole |  |  |  | 0 | 0 | 0
| Face area |  |  | m² | 1.131 | 1.131 | 1.131
| Fin |  | Treatment |  | Anti-corrosion treatment (PE) | Anti-corrosion treatment (PE) | Anti-corrosion treatment (PE)
|  |  | Type |  | WF fin | WF fin | WF fin
| Fin pitch |  |  | mm | 1,4 | 1,4 | 1,4
| Length |  |  | mm | 857 | 857 | 857
| Passes |  | Quantity |  | 5 | 5 | 5
| Rows |  | Quantity |  | 2 | 2 | 2
| Stages |  | Quantity |  | 60 | 60 | 60
Pump Standard | Nominal ESP unit |  | Cooling | kPa | 60.5 | 57.8 | 53.2
|  |  | Heating | kPa | 57.1 | 52.5 | 47.3
| Nr of speeds |  |  |  | 2 | 2 | 2
| Model |  |  |  | STRATOS PARA 25/1-8 | STRATOS PARA 25/1-8 | STRATOS PARA 25/1-8
| Power input |  |  | W | 210 | 210 | 210
| Type |  |  |  | Water cooled | Water cooled | Water cooled
Hydraulic components | Expansion vessel |  | Max. water pressure | bar | 3 | 3 | 3
|  |  | Pre pressure | bar | 1 | 1 | 1
|  |  | Volume | l | 10 | 10 | 10
| Water filter |  | Diameter perforations | mm | 1 | 1 | 1
|  |  | Material |  | Brass | Brass | Brass
Fan | Quantity |  |  |  | 2 | 2 | 2
| Type |  |  |  | Propeller fan | Propeller fan | Propeller fan
| Air flow rate | Cooling | Nom. | m³/min | 96.0 | 100 | 97.0
|  | Heating | Nom. | m³/min | 90.0 | 90.0 | 90.0
| Discharge direction |  |  |  | Horizontal | Horizontal | Horizontal
Fan motor | Drive |  |  |  | Direct drive | Direct drive | Direct drive
| Model |  |  |  | Brushless DC motor | Brushless DC motor | Brushless DC motor
| Output |  |  | W | 70 | 70 | 70
| Quantity |  |  |  | 2 | 2 | 2
| Speed | Cooling | Nom. | rpm | 780 | 780 | 780
|  | Heating | Nom. | rpm | 760 | 760 | 760
|  |  | Steps |  | 8 | 8 | 8
Refrigerant oil | Type |  |  |  | Daphne FVC68D | Daphne FVC68D | Daphne FVC68D
| Charged volume |  |  | l | 1.00 | 1.00 | 1.00
Compressor | Quantity |  |  |  | 1 | 1 | 1
| Type |  |  |  | Hermetically sealed scroll compressor | Hermetically sealed scroll compressor | Hermetically sealed scroll compressor
| Model |  |  |  | JT100G-VD | JT100G-VD | JT100G-VD
| Motor (INV) |  | Crankcase heater | W | 33.0 | 33.0 | 33.0
| Output |  |  | W | 2,200 | 2,200 | 2,200
| Starting method |  |  |  | Inverter driven | Inverter driven | Inverter driven
Operation range | Air side | Cooling | Max. | °CDB | 46 | 46 | 46
|  |  | Min. | °CDB | 10 | 10 | 10
|  | Heating | Max. | °CDB | 35 | 35 | 35
|  |  | Min. | °CDB | -15 | -15 | -15
| Water side | Cooling | Max. | °CDB | 20 | 20 | 20
|  |  | Min. | °CDB | 5 | 5 | 5
|  | Heating | Max. | °CDB | 50 (5) | 50 (5) | 50 (5)
|  |  | Min. | °CDB | 30 (5) | 30 (5) | 30 (5)
Sound power level | Cooling |  | Nom. | dBA | 64.0 (3) | 64.0 (3) | 64.0 (3)
| Heating |  | Nom. | dBA | 60 (2) | 64 (4) | 60 (4)
Sound pressure level | Cooling |  | Nom. | dBA | 50 (3) | 50 (3) | 50 (3)
| Heating |  | Nom. | dBA | 50 (3) | 50 (3) | 50 (3)
| Night quiet mode |  | Cooling | dBA | 45 | 45 | 45
|  |  | Heating | dBA | 42 | 42 | 42
Refrigerant | Type |  |  |  | R-410A | R-410A | R-410A
| GWP |  |  |  | 2,087.5 | 2,087.5 | 2,087.5
| Circuits |  | Quantity |  | 1 | 1 | 1
| Control |  |  |  | Electronic expansion valve | Electronic expansion valve | Electronic expansion valve
Charge | Per circuit |  |  | kg | 2.95 | 2.95 | 2.95
| Per circuit |  |  | TCO2Eq | 6.16 | 6.16 | 6.16
Water circuit | Air purge valve |  |  |  | Yes | Yes | Yes
| Drain valve / fill valve |  |  |  | Yes | Yes | Yes
| Manometer |  |  |  | Yes | Yes | Yes
| Minimum water volume in the system |  |  | l | 20 (6) | 20 (6) | 20 (6)
| Piping |  |  | inch | 5/4" | 5/4" | 5/4"
| Piping connections diameter |  |  | inch | G 5/4" (female) | G 5/4" (female) | G 5/4" (female)
| Safety valve |  |  | bar | 3 | 3 | 3
| Shut off valve |  |  |  | Yes | Yes | Yes
| Total water volume |  |  | l | 4.00 (5) | 4.00 (5) | 4.00 (5)
Defrost control |  |  |  |  | Sensor for outdoor heat exchanger temperature | Sensor for outdoor heat exchanger temperature | Sensor for outdoor heat exchanger temperature
Defrost method |  |  |  |  | Pressure equalising | Pressure equalising | Pressure equalising
Safety devices | Item |  | 01 |  | High pressure switch | High pressure switch | High pressure switch
|  |  | 02 |  | Fan motor thermal protection | Fan motor thermal protection | Fan motor thermal protection
|  |  | 03 |  | Fuse | Fuse | Fuse
General | Supplier/Manufacturer details |  | Name and address |  | Daikin Europe N.V. - Zandvoordestraat 300, 8400 Oostende, Belgium | Daikin Europe N.V. - Zandvoordestraat 300, 8400 Oostende, Belgium | Daikin Europe N.V. - Zandvoordestraat 300, 8400 Oostende, Belgium
|  |  | Name or trademark |  | Daikin Europe N.V. | Daikin Europe N.V. | Daikin Europe N.V.
| Product description |  | Air-to-water heat pump |  | Yes | Yes | Yes
|  |  | Brine-to-water heat pump |  | No | No | No
|  |  | Heat pump combination heater |  | No | No | No
|  |  | Low-temperature heat pump |  | Yes | Yes | Yes
|  |  | Supplementary heater integrated |  | Yes | Yes | Yes
|  |  | Water-to-water heat pump |  | No | No | No
LW(A) Sound power level (according to EN14825) | dB(A) |  |  |  | 64.0 | 64.0 | 64.0
Sound condition Ecodesign and energy label |  |  |  |  | Sound power in heating mode, measured according to the EN12102 under conditions of the EN14825 | Sound power in heating mode, measured according to the EN12102 under conditions of the EN14825 | Sound power in heating mode, measured according to the EN12102 under conditions of the EN14825
Space heating general | Air to water unit |  | Rated airflow (outdoor) | m³/h | 5,400 | 5,400 | 5,400
| Other |  | Capacity control |  | Inverter | Inverter | Inverter
|  |  | Cdh (Degradation heating) |  | 1.00 | 1.00 | 1.00
|  |  | Pck (Crankcase heater mode) | kW | 0.050 | 0.050 | 0.050
|  |  | Poff (Off mode) | kW | 0.049 | 0.049 | 0.049
|  |  | Psb (Standby mode) | kW | 0.049 | 0.049 | 0.049
|  |  | Pto (Thermostat off) | kW | 0.186 | 0.186 | 0.186
| Integrated supplementary heater |  | NOx emission | mg/kWh | 0.00 | 0.00 | 0.00
|  |  | Psup | kW | 0.00 | 0.00 | 0.00
|  |  | Type of energy input |  | Electrical | Electrical | Electrical
Space heating | Average climate water outlet 35°C | General | Annual energy consumption | kWh | 6,140 | 6,810 | 7,920
|  |  | Ƞs (Seasonal space heating efficiency) | % | 126 | 131 | 134
|  |  | Prated at -10°C | kW | 10.2 | 11.7 | 13.8
|  |  | Qhe Annual energy consumption (GCV) | Gj | 22.1 | 24.5 | 28.5
|  |  | SCOP |  | 3.22 | 3.34 | 3.41
|  |  | Seasonal space heating eff. class |  | A+ | A+ | A+
|  | A Condition (-7°CDB/-8°CWB) | COPd |  | 2.83 | 2.89 | 2.88
|  |  | Pdh | kW | 6.80 | 8.00 | 9.60
|  |  | PERd | % | 113 | 116 | 115
|  | B Condition (2°CDB/1°CWB) | Cdh (Degradation heating) |  | 1.00 | 1.00 | 1.00
|  |  | COPd |  | 3.74 | 3.84 | 3.64
|  |  | Pdh | kW | 5.50 | 6.50 | 7.60
|  |  | PERd | % | 150 | 154 | 146
|  | C Condition (7°CDB/6°CWB) | Cdh (Degradation heating) |  | 1.00 | 1.00 | 1.00
|  |  | COPd |  | 4.44 | 4.49 | 4.65
|  |  | Pdh | kW | 4.60 | 4.60 | 4.90
|  |  | PERd | % | 178 | 180 | 186
|  | D Condition (12°CDB/11°CWB) | Cdh (Degradation heating) |  | 1.00 | 1.00 | 1.00
|  |  | COPd |  | 5.31 | 5.59 | 5.76
|  |  | Pdh | kW | 5.30 | 5.30 | 5.20
|  |  | PERd | % | 212 | 224 | 230
|  | Rated heat output supplementary capacity | Psup (at Tdesign -10°C) | kW | 4.00 | 4.50 | 4.90
|  | Tbiv (bivalent temperature) | COPd |  | 3.11 | 3.11 | 3.21
|  |  | Pdh | kW | 6.90 | 7.70 | 9.60
|  |  | PERd | % | 124 | 124 | 128
|  |  | Tbiv | °C | -2.00 | -2.00 | -2.00
|  | Tol (temperature operating limit) | COPd |  | 2.49 | 2.55 | 2.57
|  |  | Pdh | kW | 6.20 | 7.30 | 8.90
|  |  | PERd | % | 99.6 | 102 | 103
|  |  | TOL | °C | -10.0 | -10.0 | -10.0
|  |  | WTOL | °C | 35.0 | 35.0 | 35.0
| Cold climate water outlet 35°C | General | Annual energy consumption | kWh | 7,660 | 8,730 | 9,700
|  |  | Ƞs (Seasonal space heating efficiency) | % | 108 | 108 | 113
|  |  | Prated at -22°C | kW | 9.00 | 10.1 | 11.7
|  |  | Qhe Annual energy consumption (GCV) | Gj | 27.6 | 31.4 | 34.9
| Warm climate water outlet 35°C | General | Annual energy consumption | kWh | 2,230 | 2,460 | 2,660
|  |  | Ƞs (Seasonal space heating efficiency) | % | 137 | 147 | 156
|  |  | Prated at 2°C | kW | 7.30 | 8.50 | 9.50
|  |  | Qhe Annual energy consumption (GCV) | Gj | 8.03 | 8.85 | 9.57
Power supply | Name |  |  |  | V3 | V3 | V3
| Phase |  |  |  | 1~ | 1~ | 1~
| Frequency |  |  | Hz | 50 | 50 | 50
| Voltage |  |  | V | 230 | 230 | 230
| Voltage range |  | Min. | % | -10 | -10 | -10
|  |  | Max. | % | 10 | 10 | 10
Unit | Minimum Ssc value |  |  |  | Equipment complying with EN/IEC 61000-3-12 | Equipment complying with EN/IEC 61000-3-12 | Equipment complying with EN/IEC 61000-3-12
| Recommended fuses |  |  | A | 32 | 32 | 32
Compressor | Starting method |  |  |  | Inverter driven | Inverter driven | Inverter driven
| Crankcase heater |  |  | W | 33 | 33 | 33
Wiring connections | General |  |  |  | See installation manual | See installation manual | See installation manual
Notes |  |  |  |  | Underfloor program: cooling Ta 35°C - LWE 18°C (Dt: 5°C); heating Ta DB/WB 7°C/6°C - LWC 35°C (Dt: 5°C) | Underfloor program: cooling Ta 35°C - LWE 18°C (Dt: 5°C); heating Ta DB/WB 7°C/6°C - LWC 35°C (Dt: 5°C) | Underfloor program: cooling Ta 35°C - LWE 18°C (Dt: 5°C); heating Ta DB/WB 7°C/6°C - LWC 35°C (Dt: 5°C)
[5 empty] | Fan coil program: cooling Ta 35°C - LWE 7°C ( Dt: 5°C); heating Ta DB/WB 7°C/6°C - LWC 45°C ( Dt: 5°C ) | Fan coil program: cooling Ta 35°C - LWE 7°C ( Dt: 5°C); heating Ta DB/WB 7°C/6°C - LWC 45°C ( Dt: 5°C ) | Fan coil program: cooling Ta 35°C - LWE 7°C ( Dt: 5°C); heating Ta DB/WB 7°C/6°C - LWC 45°C ( Dt: 5°C )
[5 empty] | Condition: Ta 35°C - LWE 7°C ( DT = 5°C) | Condition: Ta 35°C - LWE 7°C ( DT = 5°C) | Condition: Ta 35°C - LWE 7°C ( DT = 5°C)
[5 empty] | Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C) | Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C) | Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)
[5 empty] | Including piping + PHE; excluding expansion vessel | Including piping + PHE; excluding expansion vessel | Including piping + PHE; excluding expansion vessel
[5 empty] | Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info. | Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info. | Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info.
[5 empty] | Contains fluorinated greenhouse gases | Contains fluorinated greenhouse gases | Contains fluorinated greenhouse gases