## Products
PRODUCT NAME | EWYQ-G-XS
[5 empty] | EWYQ075G-XS | EWYQ085G-XS | EWYQ100G-XS | EWYQ110G-XS | EWYQ120G-XS | EWYQ140G-XS | EWYQ160G-XS
Cooling capacity | Nom. |  |  | kW | 77.8 (1) | 88.1 (1) | 101 (1) | 117 (1) | 127 (1) | 147 (1) | 165 (1)
Heating capacity | Nom. |  |  | kW | 82.2 (2) | 91.2 (2) | 110 (2) | 127 (2) | 138 (2) | 156 (2) | 170 (2)
Capacity control | Method |  |  |  | Step | Step | Step | Step | Step | Step | Step
| Minimum capacity |  |  | % | 50 | 44 | 50 | 44 | 50 | 43 | 50
Power input | Cooling |  | Nom. | kW | 27.0 (1) | 31.5 (1) | 36.0 (1) | 39.5 (1) | 44.7 (1) | 50.2 (1) | 57.8 (1)
| Heating |  | Nom. | kW | 26 (2) | 29 (2) | 34 (2) | 39 (2) | 43 (2) | 50 (2) | 54 (2)
EER |  |  |  |  | 2.88 (1) | 2.80 (1) | 2.81 (1) | 2.97 (1) | 2.84 (1) | 2.92 (1) | 2.85 (1)
COP |  |  |  |  | 3.14 (2) | 3.12 (2) | 3.24 (2) | 3.25 (2) | 3.20 (2) | 3.11 (2) | 3.13 (2)
ESEER |  |  |  |  | 3.90 | 3.94 | 3.97 | 4.03 | 3.92 | 3.96 | 3.96
IPLV |  |  |  |  | 4.40 | 4.47 | 4.40 | 4.49 | 4.40 | 4.50 | 4.50
SCOP |  |  |  |  | 3.35 (3) | 3.31 (3) | 3.62 (3) | 3.56 (3) | 3.63 (3) | 3.53 (3) | 3.58 (3)
Dimensions | Unit |  | Depth | mm | 2,826 | 2,826 | 2,826 | 3,426 | 3,426 | 4,026 | 4,026
|  |  | Height | mm | 1,800 | 1,800 | 1,800 | 1,800 | 1,800 | 1,800 | 1,800
|  |  | Width | mm | 1,195 | 1,195 | 1,195 | 1,195 | 1,195 | 1,195 | 1,195
Weight | Operation weight |  |  | kg | 858 | 921 | 1,088 | 1,194 | 1,224 | 1,344 | 1,411
| Unit |  |  | kg | 850 | 912 | 1,077 | 1,183 | 1,213 | 1,333 | 1,394
Casing | Colour |  |  |  | Ivory white | Ivory white | Ivory white | Ivory white | Ivory white | Ivory white | Ivory white
| Material |  |  |  | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet | Galvanized and painted steel sheet
Water heat exchanger | Type |  |  |  | Brazed plate | Brazed plate | Brazed plate | Brazed plate | Brazed plate | Brazed plate | Brazed plate
| Water flow rate | Cooling | Nom. | l/s | 3.7 | 4.2 | 4.8 | 5.6 | 6.1 | 7.0 | 7.9
|  | Heating | Nom. | l/s | 4.0 | 4.4 | 5.3 | 6.1 | 6.7 | 7.5 | 8.2
| Water pressure drop | Cooling | Nom. | kPa | 8.40 | 8.30 | 8.70 | 11.6 | 13.7 | 18.2 | 19.9
|  | Heating | Nom. | kPa | 9.50 | 9.10 | 11.2 | 14.4 | 17.2 | 21.7 | 22.5
| Water volume |  |  | l | 8.10 | 9.40 | 10.8 | 10.8 | 10.8 | 10.8 | 16.7
| Insulation material |  |  |  | Closed cell | Closed cell | Closed cell | Closed cell | Closed cell | Closed cell | Closed cell
Air heat exchanger | Type |  |  |  | High efficiency fin and tube type | High efficiency fin and tube type | High efficiency fin and tube type | High efficiency fin and tube type | High efficiency fin and tube type | High efficiency fin and tube type | High efficiency fin and tube type
Fan | Quantity |  |  |  | 6 | 6 | 6 | 8 | 8 | 10 | 10
| Type |  |  |  | Direct propeller | Direct propeller | Direct propeller | Direct propeller | Direct propeller | Direct propeller | Direct propeller
| Air flow rate |  | Nom. | l/s | 10,042 | 10,042 | 9,861 | 13,148 | 13,148 | 16,435 | 16,435
| Diameter |  |  | mm | 450 | 450 | 450 | 450 | 450 | 450 | 450
| Speed |  |  | rpm | 1,360 | 1,360 | 1,360 | 1,360 | 1,360 | 1,360 | 1,360
Fan motor | Drive |  |  |  | Direct on line | Direct on line | Direct on line | Direct on line | Direct on line | Direct on line | Direct on line
| Input |  | Cooling | W | 2,700.0 | 2,700.0 | 2,700.0 | 3,600.0 | 3,600.0 | 4,500.0 | 4,500.0
Compressor | Quantity |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Type |  |  |  | Scroll compressor | Scroll compressor | Scroll compressor | Scroll compressor | Scroll compressor | Scroll compressor | Scroll compressor
| Oil |  | Charged volume | l | 6.80 | 8.10 | 9.30 | 11.5 | 13.6 | 13.1 | 12.6
| Starting method |  |  |  | Direct on line | Direct on line | Direct on line | Direct on line | Direct on line | Direct on line | Direct on line
Operation range | Air side | Cooling | Max. | °CDB | 45 | 45 | 45 | 45 | 45 | 45 | 45
|  |  | Min. | °CDB | -10 | -10 | -10 | -10 | -10 | -10 | -10
|  | Heating | Max. | °CDB | 45 | 45 | 45 | 45 | 45 | 45 | 45
|  |  | Min. | °CDB | -10 | -10 | -10 | -10 | -10 | -10 | -10
| Water side | Cooling | Max. | °CDB | 15 | 15 | 15 | 15 | 15 | 15 | 15
|  |  | Min. | °CDB | -10 | -10 | -10 | -10 | -10 | -10 | -10
|  | Heating | Max. | °CDB | 15 | 15 | 15 | 15 | 15 | 15 | 15
|  |  | Min. | °CDB | -10 | -10 | -10 | -10 | -10 | -10 | -10
Sound power level | Cooling |  | Nom. | dBA | 84 | 85 | 87 | 89 | 89 | 89 | 89
Sound pressure level | Cooling |  | Nom. | dBA | 66 | 68 | 70 | 71 | 71 | 71 | 71
Refrigerant | Type |  |  |  | R-410A | R-410A | R-410A | R-410A | R-410A | R-410A | R-410A
| GWP |  |  |  | 2,087.5 | 2,087.5 | 2,087.5 | 2,087.5 | 2,087.5 | 2,087.5 | 2,087.5
| Circuits |  | Quantity |  | 1 | 1 | 1 | 1 | 1 | 1 | 1
Charge | Per circuit |  |  | kg | 17.0 | 17.7 | 23.5 | 29.4 | 28.3 | 32.0 | 34.9
| Per circuit |  |  | TCO2Eq | 35.5 | 36.9 | 49.1 | 61.4 | 59.1 | 66.8 | 72.9
Piping connections | Evaporator water inlet/outlet (OD) |  |  |  | 2" 1/2 | 2" 1/2 | 2" 1/2 | 2" 1/2 | 2" 1/2 | 2" 1/2 | 2" 1/2
General | Supplier/Manufacturer details |  | Name and address |  | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy | Daikin Applied Europe - Via Piani di S.Maria 72, 00040 Ariccia (Roma), Italy
|  |  | Name or trademark |  | Daikin Applied Europe | Daikin Applied Europe | Daikin Applied Europe | Daikin Applied Europe | Daikin Applied Europe | Daikin Applied Europe | Daikin Applied Europe
| Product description |  | Air-to-water heat pump |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes
|  |  | Brine-to-water heat pump |  | No | No | No | No | No | No | No
|  |  | Heat pump combination heater |  | No | No | No | No | No | No | No
|  |  | Low-temperature heat pump |  | No | No | No | No | No | No | No
|  |  | Supplementary heater integrated |  | No | No | No | No | No | No | No
|  |  | Water-to-water heat pump |  | No | No | No | No | No | No | No
LW(A) Sound power level (according to EN14825) | dB(A) |  |  |  | 84 | 85 | 87 | 89 | 89 | 89 | 89
Space heating general | Other |  | Capacity control |  | Staged | Staged | Staged | Staged | Staged | Staged | Staged
|  |  | Cdh (Degradation heating) |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Space heating | Average climate water outlet 35°C | General | Annual energy consumption | kWh | 49,231 | 59,098 | 57,504 | 62,371 | 58,987 | 68,347 | 73,151
|  |  | Ƞs (Seasonal space heating efficiency) | % | 131 | 129 | 142 | 140 | 142 | 138 | 140
|  |  | Prated at -10°C | kW | 79.9 | 94.7 | 101 | 108 | 104 | 117 | 127
|  |  | SCOP |  | 3.35 | 3.31 | 3.62 | 3.58 | 3.63 | 3.53 | 3.58
|  | A Condition (-7°CDB/-8°CWB) | COPd |  | 2.50 | 2.47 | 2.61 | 2.60 | 2.58 | 2.50 | 2.48
|  |  | Pdh | kW | 53.9 | 59.5 | 73.1 | 83.5 | 91.6 | 103.2 | 112.3
|  |  | PERd | % | 100.0 | 100.0 | 100.0 | 100.0 | 100.0 | 100.0 | 100.0
|  | B Condition (2°CDB/1°CWB) | Cdh (Degradation heating) |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | COPd |  | 3.22 | 3.23 | 3.46 | 3.38 | 3.41 | 3.30 | 3.38
|  |  | Pdh | kW | 43.1 | 51.2 | 54.5 | 58.3 | 60.4 | 68.0 | 74.0
|  |  | PERd | % | 65.0 | 70.5 | 60.0 | 55.0 | 48.0 | 49.0 | 49.0
|  | C Condition (7°CDB/6°CWB) | Cdh (Degradation heating) |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | COPd |  | 4.58 | 4.71 | 4.94 | 4.75 | 4.60 | 4.50 | 4.57
|  |  | Pdh | kW | 28.0 | 33.2 | 35.4 | 37.9 | 36.4 | 41.1 | 44.7
|  |  | PERd | % | 37.0 | 40.0 | 34.0 | 31.0 | 27.0 | 27.0 | 27.0
|  | D Condition (12°CDB/11°CWB) | Cdh (Degradation heating) |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | COPd |  | 5.25 | 5.43 | 5.60 | 5.21 | 5.12 | 5.02 | 5.07
|  |  | Pdh | kW | 12.0 | 14.2 | 15.2 | 16.3 | 15.6 | 17.6 | 19.2
|  |  | PERd | % | 13.0 | 14.0 | 12.0 | 10.0 | 8.3 | 8.1 | 8.2
|  | Rated heat output supplementary capacity | Psup (at Tdesign -10°C) | kW | 26.2 | 35.3 | 27.6 | 25.0 | 12.4 | 13.2 | 14.0
|  | Tbiv (bivalent temperature) | COPd |  | 3.22 | 3.20 | 3.27 | 3.16 | 2.95 | 2.86 | 2.84
|  |  | Pdh | kW | 58.4 | 65.6 | 77.6 | 87.2 | 91.6 | 103.2 | 112.3
|  |  | PERd | % | 100.0 | 100.0 | 100.0 | 100.0 | 100.0 | 100.0 | 100.0
|  |  | Tbiv | °C | -3 | -2 | -4 | -5 | -7 | -7 | -7
|  | Tol (temperature operating limit) | COPd |  | 2.46 | 2.44 | 2.59 | 2.56 | 2.55 | 2.48 | 2.45
|  |  | Pdh | kW | 53.6 | 59.4 | 73.3 | 82.9 | 91.2 | 103.5 | 112.9
|  |  | PERd | % | 100.0 | 100.0 | 100.0 | 100.0 | 100.0 | 100.0 | 100.0
|  |  | TOL | °C | -10 | -10 | -10 | -10 | -10 | -10 | -10
|  |  | WTOL | °C | 45 | 45 | 45 | 45 | 45 | 45 | 45
Power supply | Phase |  |  |  | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~
| Frequency |  |  | Hz | 50 | 50 | 50 | 50 | 50 | 50 | 50
| Voltage |  |  | V | 400 | 400 | 400 | 400 | 400 | 400 | 400
| Voltage range |  | Min. | % | -10 | -10 | -10 | -10 | -10 | -10 | -10
|  |  | Max. | % | 10 | 10 | 10 | 10 | 10 | 10 | 10
Unit | Starting current |  | Max | A | 213 | 264 | 270 | 319 | 327 | 367 | 381
| Running current | Cooling | Nom. | A | 52 | 56 | 60 | 69 | 76 | 88 | 95
|  |  | Max | A | 70 | 75 | 81 | 91 | 99 | 116 | 131
| Max unit current for wires sizing |  |  | A | 77 | 83 | 89 | 100 | 109 | 128 | 144
Fans | Nominal running current (RLA) |  |  | A | 6 | 6 | 6 | 8 | 8 | 10 | 10
Compressor | Phase |  |  |  | 3~ | 3~ | 3~ | 3~ | 3~ | 3~ | 3~
| Voltage |  |  | V | 400 | 400 | 400 | 400 | 400 | 400 | 400
| Voltage range |  | Min. | % | -10 | -10 | -10 | -10 | -10 | -10 | -10
|  |  | Max. | % | 10 | 10 | 10 | 10 | 10 | 10 | 10
| Maximum running current |  |  | A | 62 | 67 | 73 | 81 | 89 | 104 | 119
| Starting method |  |  |  | Direct on line | Direct on line | Direct on line | Direct on line | Direct on line | Direct on line | Direct on line
Notes |  |  |  |  | Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation. | Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation. | Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation. | Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation. | Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation. | Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation. | Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.
[5 empty] | Heating capacity, unit power input and COP are based on the following conditions: ambient 7°C; condenser 40.0/45.0°C, unit at full load operation | Heating capacity, unit power input and COP are based on the following conditions: ambient 7°C; condenser 40.0/45.0°C, unit at full load operation | Heating capacity, unit power input and COP are based on the following conditions: ambient 7°C; condenser 40.0/45.0°C, unit at full load operation | Heating capacity, unit power input and COP are based on the following conditions: ambient 7°C; condenser 40.0/45.0°C, unit at full load operation | Heating capacity, unit power input and COP are based on the following conditions: ambient 7°C; condenser 40.0/45.0°C, unit at full load operation | Heating capacity, unit power input and COP are based on the following conditions: ambient 7°C; condenser 40.0/45.0°C, unit at full load operation | Heating capacity, unit power input and COP are based on the following conditions: ambient 7°C; condenser 40.0/45.0°C, unit at full load operation
[5 empty] | SCOP is based on the following conditions:Tbivalent -3°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825 | SCOP is based on the following conditions:Tbivalent -3°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825 | SCOP is based on the following conditions:Tbivalent -3°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825 | SCOP is based on the following conditions:Tbivalent -3°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825 | SCOP is based on the following conditions:Tbivalent -3°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825 | SCOP is based on the following conditions:Tbivalent -3°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825 | SCOP is based on the following conditions:Tbivalent -3°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825
[5 empty] | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units | Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units
[5 empty] | Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water | Fluid: Water
[5 empty] | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS). | For more details on the operating limits please refer to the Chiller Selection Software (CSS).
[5 empty] | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels. | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels. | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels. | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels. | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels. | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels. | Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.
[5 empty] | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%. | Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.
[5 empty] | Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced. | Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced. | Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced. | Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced. | Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced. | Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced. | Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.
[5 empty] | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current. | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current. | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current. | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current. | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current. | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current. | Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.
[5 empty] | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current | Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current
[5 empty] | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage. | Maximum unit current for wires sizing is based on minimum allowed voltage.
[5 empty] | Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1 | Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1 | Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1 | Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1 | Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1 | Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1 | Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1
[5 empty] | The sound pressure level is calculated from the sound power level and is for information only and not considered binding | The sound pressure level is calculated from the sound power level and is for information only and not considered binding | The sound pressure level is calculated from the sound power level and is for information only and not considered binding | The sound pressure level is calculated from the sound power level and is for information only and not considered binding | The sound pressure level is calculated from the sound power level and is for information only and not considered binding | The sound pressure level is calculated from the sound power level and is for information only and not considered binding | The sound pressure level is calculated from the sound power level and is for information only and not considered binding
[5 empty] | Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1 | Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1 | Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1 | Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1 | Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1 | Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1 | Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1
[5 empty] | Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511) | Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511) | Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511) | Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511) | Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511) | Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511) | Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511)
[5 empty] | Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory | Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory | Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory | Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory | Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory | Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory | Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory
[5 empty] | For specific information about additional options refer to the options section in the data book | For specific information about additional options refer to the options section in the data book | For specific information about additional options refer to the options section in the data book | For specific information about additional options refer to the options section in the data book | For specific information about additional options refer to the options section in the data book | For specific information about additional options refer to the options section in the data book | For specific information about additional options refer to the options section in the data book